McDevitt Middle School

TESTING AND BALANCING

For the City of Waltham

October, 16, 2009
MCDEVITT MIDDLE SCHOOL
REQUEST FOR PROPOSAL (RFP)

TESTING AND BALANCING

The City of Waltham, MA, the Owner and Awarding Authority, is soliciting proposals for testing and balancing services for the McDevitt Middle School. The project consists of a 121,000 SF building; that was constructed in 2002.

The firm engaged will work with the Waltham Public Schools in concert with the Owners' Facilities Director. Most all work will be performed after normal schools hours (7a.m.-3p.m.). Some work can scheduled during non schools days with the prior approval of the Facilities Director.
The owner will award one Contract for testing and balancing services. The selected

Proposer shall be responsible for providing all identified testing and balancing for this project.

PROPOSAL SUBMISSION REQUIREMENTS

A. Time Date and Place for Proposal Submission: Proposals must be submitted to the Office of Purchasing, James McGrath, City Hall, 610 Main Street, Waltham, MA 02452 by 10:00 AM local time,_________________________.

B. Time for Acceptance:. The Contract for testing and balancing will be awarded by the Awarding Authority.

C. Price and Non-Price Proposals: It is a mandatory requirement that the Proposer submit both a Price and a Non-Price Proposal. Each proposal shall be sealed in a separate envelope and submitted to the Awarding Authority by the required submission date.

D. Plan of Service: The Proposer shall include in the Non-Price Proposal a written description of his/her approach to providing required testing and balancing services. He/She shall provide a schedule indicating anticipated testing and balancing requirements for this project.

E. Minimum Evaluation Criteria: The following criteria are minimum requirements for consideration for this Contract:
1. 
The Proposer shall have been in business as a Testing and Balancing Company 
for a minimum for five (5) years.

2.

The Proposer shall provide all qualified personnel. All personnel must have a 
minimum of three (3) years of experience in testing and balancing. Evidence of 
personnel experience must be provided in the proposal.
3.

The Proposer shall provide a qualified project supervisor with at least five (5) years 
of experience in testing and balancing service.

4.

The Proposer shall provide evidence of Professional Liability Insurance (errors and   
omissions) and Automobile Liability Insurance and Workman's Compensation.

McDevitt Middle School
Testing & Balancing RFP
Page 1

Insurance
The insurance carried by the Contractor shall be written for not less than the limits of liability required by law or the following limits, whichever is greater:

a. State and Federal Workman's Compensation: Statutory requirements in accordance with the laws of the Commonwealth of Massachusetts.

b.
   PROFESSIONAL LIABILITY

Each Occurrence
$1,000,000

Aggregate
$3,000,000

AUTOMOBILE LIABILITY

Bodily Injury Per Accident
$1,000,000

Property Damage per Accident
$1,000,000

Provide coverage for all owned, non-owned and hired vehicles

EXCESS LIABILITY (UMBRELLA COVERAGE)

Each Occurrence
$5,000,000.

Aggregate
$5,000,000

The City of Waltham shall be named as an Additional Insured on all liability policies. The party to whom the contract is awarded shall furnish proof of such coverage to the Awarding Authority at the time of execution of the contract. If the proposed does not normally carry insurance in the amounts shown, provide standard coverage amounts and identify additional premium costs to increase coverage to specified amounts in the proposal.

5.       The Proposer shall provide a reverence list of projects of comparable scope that his or her company has performed. The Proposer shall include with the reference list the name of the project Architect or Engineer and the name and telephone number of any Owner's representative.

OWNER'S RIGHT TO REJECT PROPOSAL(S)

The Awarding Authority reserves the right to reject any or all proposals. PRICE PROPOSAL

The Proposer shall submit a separate Price Proposal to the Office of Purchasing, James McGrath (in a separate envelope). The phrase "Price Proposal" must be clearly printed on the outside of the envelope. The proposed price is a lump sum including all hours, visits, tests, travel, mileage and reports to complete the Scope of Work in the attached Section 15950.
McDevitt Middle School
Testing & Balancing RFP
Page 2
          MCDEVITT MIDDLE SCHOOL
10/16/09
SECTION 15950 - TESTING, ADJUSTING, AND BALANCING (TAB)

	PART I – GENERAL
	

	PARA. NO.
DESCRIPTION
	PAGE NO.

	1.1
GENERAL
	15950-01

	1.2
RELATED DOCUMENTS
	15950-02

	1.3
SUMMARY
	15950-02

	1.4
DEFINITIONS
	15950-02

	1.5
SUBMITTALS
	15950-03

	1.6
QUALITY ASSURANCE
	15950-03

	1.7
PROJECT CONDITIONS
	15950-04

	1.8
COORDINATION
	15950-05

	1.9
WARRANTY
	15950-05.


PART 2- PRODUCTS (Not Applicable)

	PART 3- EXECUTION
	

	PARA.
	NO.
DESCRIPTION
	PAGE NO.

	3.1
	EXAMINATION
	15950-05.

	3.2
	PREPARATION
	15950-07

	3.3
	GENERAL PROCEDURES FOR TESTING AND BALANCING
	15950-07

	3.4
	GENERAL PROCEDURES FOR BALANCING AIR SYSTEMS
	15950-08

	3.5
	PROCEDURES FOR CONSTANT-VOLUME AIR SYSTEMS
	15950-08

	3.6
	PROCEDURES FOR VARIABLE-AIR-VOLUME SYSTEMS
	15950-10

	3.7
	GENERAL PROCEDURES FOR HYDRONIC SYSTEMS
	15950-12

	3.8
	PROCEDURES FOR HYDRONIC SYSTEMS
	15950-12

	3.9
	PROCEDURES FOR VARIABLE FLOW HYDRONIC SYSTEMS
	15950-13

	3.10
	PROCEDURES FOR MOTORS
	15950-13

	3.11
	PROCEDURES FOR CHILLER
	15950-14

	3.12
	PROCEDURES FOR CONDENSING UNITS
	15950-14

	3.13
	PROCEDURES FOR BOILERS
	15950-14

	3.14
	PROCEDURES FOR BEAT-TRANSFER COILS
	15950-15

	3.15
	PROCEDURES FOR TEMPERATURE MEASUREMENTS
	15950-15

	3.16
	TEMPERATURE-CONTROL VERIFICATION
	15950-16

	3.17
	TOLERANCES
	15950-16

	3.18
	REPORT
	15950-16

	3.19
	INSPECTIONS
	15850-30

	3.20
	ADDITIONAL TESTS
	15950-31


H:\00-18 90\Spec\15950-IX.DOC

TESTING, ADJUSTING, AND BALANCING                                                                            15950-i      
  
MCDEVITT MIDDLE SCHOOL
 10/16/09
SECTION 15950 - TESTING, ADJUSTING, AND BALANCING (TAB)

PART 1 - GENERAL

1.1
GENERAL

A. Completely balance all air, water and control systems to conform to specified quantities and to the intent of the design of the mechanical system.

B. Work shall be performed by a fully qualified and experienced System Balancing Technician.  This technician shall be named in the shop drawing submission together with a summary of his  qualifications. The technician shall spend full time on the job supervising and directing the work  listed below.

C. 
Obtain and pay for a complete set of all Contract Drawings.

D. 
For specified test openings, refer to SHEETMETAL. Provide additional openings required for pitot tube traverses. Openings shall be closed using removable gasketed plugs.

E. Where similar or typical conditions exist, submit for review, simplified checking procedures for portions of the balancing work. These procedures may be accepted if proposed procedures do not decrease the quality of the air balance.

F. Water balance shall be initiated by checking each pump BHP, and suction and discharge pressures, and pressure drops across rated equipment (e.g. chillers, unit heaters, coils, etc.).

G. Where necessary to obtain design flows, impeller diameters will be altered. Water distribution shall be checked and adjusted to all equipment by means of measuring air on and off conditions at coils and for water temperature change entering and leaving coils.

H. Control balance shall be initiated by checking, calibrating and recording the operating and sensitivity of all controls under all operating conditions.

I. Check and record air and water supply temperatures at source and at end of each system. Check and record each unit discharge air temperature with thermostat set midpoint, maximum and minimum. Correct deficiencies and record results. This procedure shall be carried out with system on all cycles.
J. Check safety controls and record control sequence. Check freeze stats using ice water. Check flow switches to ensure proper interlocking of equipment.

K. Scheduled air and water control, and changeover controls shall be checked and operation recorded by simulating complete operating cycle.

L. As part of this contract the HVAC Subcontractor shall make any changes in belts,pulley,damper and add any dampers required to provide a completely balanced system, at no expense to the owner 
TESTING, ADJUSTING, AND BALANCING                                                                     15950-1

                                              MCDEVITT MIDDLE SCHOOL                                             10/16/09
M. Perform operational tests on all motor driven equipment and run continuously for at least 40 hours. Notify Owner before test. Correct defects in noise, vibration, misalignment and in balance.

N. Refer to 15500-2.24 Sheet metal Dampers. Review all sheet metal fabrication shop drawings prior to fabrication as noted therein.

1.2
RELATED DOCUMENTS

A.     Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.3
SUMMARY

A.
This Section includes TAB to produce design objectives for the following:

1.
Air Systems

a. Constant-volume air systems.

b. Variable-air-volume systems.

2.
Hydronic Piping Systems

a. Constant-flow systems.

b. Variable-flow systems.

3.
HVAC equipment quantitative-performance settings.

4.
Verifying that automatic control devices are functioning properly.

5.
Reporting results of activities and procedures specified in this Section.

1.4
DEFINITIONS

A. Adjust: To regulate fluid flow rate and air patterns at the terminal equipment, such as to reduce fan speed or adjust a damper.

B. Balance: To proportion flows within the distribution system, including submains, branches, and terminals, according to indicated quantities.

C. Barrier or Boundary: Construction, either vertical or horizontal, such as walls, floors, and ceilings that are designed and constructed to restrict the movement of airflow, smoke, odors, and other pollutants.

D. Draft: A current of air, when referring to localized effect caused by one or more factors of high air velocity, low ambient temperature, or direction of airflow, whereby more heat is withdrawn from a person's skin than is normally dissipated.

TESTING, ADJUSTING, AND BALANCING                                                                   15950-2


MCDEVITT MIDDLE SCHOOL                                              10/16/09

E. Procedure:  An approach to and execution of a sequence of work operations to yield repeatable results.

F. RC: Room criteria.

G. Report Forms: Test data sheets for recording test data in logical order.

H. Static Head: The pressure due to the weight of the fluid above the point of measurement. In a closed system, static head is equal on both sides of the pump.

I. Suction Head: The height of fluid surface above the centerline of the pump on the suction    side.          
J. System Effect: A phenomenon that can create undesired or unpredicted conditions that cause reduced capacities in all or part of a system.

K. System Effect Factors: Allowances used to calculate a reduction of the performance ratings of a. fan when installed under conditions different from those presented when the fan was performance tested.

L. TAB: Testing, adjusting, and balancing.

M. Terminal: A point where the controlled medium, such as fluid or energy, enters or leaves the distribution system.

N. Test: A procedure to determine quantitative performance of systems or equipment.

O. Testing, Adjusting, and Balancing (TAB) Firm: The entity responsible for performing and reporting TAB procedures.

1.5
SUBMITTALS

A. Qualification Data: Within 15 days from Contractor's Notice to Proceed, submit 4 copies of evidence that TAB firm and this Project's TAB team members meet the qualifications specified in "Quality Assurance" Article. And to include references that project was completed satisfactorily.
B. Contract Documents Examination Report: Within 30 days from Contractor's Notice to Proceed, submit 4 copies of the Contract Documents review report as specified in Part 3.

C. Strategies and Procedures Plan: Within 30 days from Contractor's Notice to Proceed, submit 4 copies of TAB strategies and step-by-step procedures as specified in Part 3 "Preparation" Article. Include a complete set of report forms intended for use on this Project.

D. Certified TAB Reports: Submit two copies of reports prepared, as specified in this Section, on approved forms certified by TAB firm.

1.6
QUALITY ASSURANCE

A. TAB Firm Qualifications: TAB firm must be certified by either AABC,NEBB,or TABB.
TESTING, ADJUSTING, AND BALANCING
                                             15950-3

MCDEVITT MIDDLE SCHOOL                                       10/16/09
B. 
TAB Conference: Meet with Owner's representatives on approval of TAB strategies and procedures plan to develop a mutual understanding of the details. Ensure the participation of TAB team members, equipment manufacturers' authorized service representatives; HVAC controls installers, and other support personnel. Provide seven days' advance notice of scheduled meeting time and location.

1.
Agenda Items: Include at least the following:

a. Submittal distribution requirements.

b. The Contract Documents examination report.

c. TAB plan.

d. Work schedule and Project-site access requirements.

e. Coordination and cooperation of trades and subcontractors.

f. Coordination of documentation and communication flow.

C.
Certification of TAB Reports: Certify TAB field data reports. This certification includes the following:

1. Review field data reports to validate accuracy of data and to prepare certified TAB                    reports.

2. Certify that TAB team complied with approved TAB plan and the procedures specified and referenced in this Specification.

D. 
TAB Report Forms: Use standard forms from AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems." Or NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems."

E.
Instrumentation Type, Quantity, and Accuracy: As described in AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems."

F.
Instrumentation Calibration: Calibrate instruments at least every six months or more frequently if required by instrument manufacturer.

1.
Keep an updated record of instrument calibration that indicates date of calibration and the name of party performing instrument calibration.

1.7
PROJECT CONDITIONS

A.     Owner Occupancy: Owner will occupy building during project. Cooperate with Owner   during   TAB operations to minimize conflicts with Owner's operations.  
TESTING, ADJUSTING, AND BALANCING
                                                  15950-4      
MCDEVITT MIDDLE SCHOOL                               10/16/09

1.8
COORDINATION

A. Coordinate the efforts of factory-authorized service representatives for systems and equipment, HVAC controls installers, and other mechanics to operate HVAC systems and equipment to support and assist TAB activities.

B. Notice: Provide seven days' advance notice for each test. Include scheduled test dates and times.

C. Perform TAB after leakage and pressure tests on air and water distribution systems have been satisfactorily completed:

1.9
WARRANTY

A. 
National Project Performance Guarantee: Provide a guarantee on AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems" forms or on NEBB forms stating that AABC or TABB will assist in completing requirements of the Contract Documents if TAB firm fails to comply with the Contract Documents. Guarantee includes the following provisions:

1. The certified TAB firm has tested and balanced systems according to the Contract Documents.

2. Systems are balanced to optimum performance capabilities within design and installation limits.

PART 2 - PRODUCTS (Not Applicable)

PART 3- EXECUTION 3.1. 
EXAMINATION
A. Examine the Contract Documents to become familiar with Project requirements.

1. 
Verify that balancing devices, such as test ports, gage cocks, thermometer wells, flow-control devices, balancing valves and fittings, and manual volume dampers, are required by the Contract Documents. Verify that quantities and locations of these balancing devices are accessible and appropriate for effective balancing and for efficient system and equipment operation.

B. 
Examine approved submittal data of HVAC systems and equipment.

C. 
Examine Project Record Documents described in Division 1 Section "Project Record Documents."

D. 
Examine equipment performance data including fan and pump curves. Relate performance data to Project conditions and requirements, including system effects that can create undesired or unpredicted conditions that cause reduced capacities in all or part of a system. Calculate system

TESTING, ADJUSTING, AND BALANCING                                                                         15950-5
MCDEVITT MIDDLE SCHOOL                                           10/16/09

effect factors to reduce performance ratings of HVAC equipment when installed under conditions different from those presented when the equipment was performance tested at the factory. To calculate system effects for air systems, use tables and charts found in AMCA 201, "Fans and Systems," Sections 7 through 10; or in SMACNA's "HVAC Systems--Duct Design," Sections 5 and 6. Compare this data with the design data and installed conditions.

E. Examine system and equipment installations to verify that they are complete and that testing, cleaning, adjusting, and commissioning specified in individual Sections have been performed.

F. Examine system and equipment test reports.

G. Examine HVAC system and equipment installations to verify that indicated balancing devices, such as test ports, gage cocks, thermometer wells, flow-control devices, balancing valves and fittings, and manual volume dampers, are properly installed, and that their locations are accessible and appropriate for effective balancing and for efficient system and equipment operation.

H. Examine systems for functional deficiencies that cannot be corrected by adjusting and balancing.

I. Examine HVAC equipment to ensure that clean filters have been installed, bearings are greased, belts are aligned and tight, and equipment with functioning controls is ready for operation.

J. Examine terminal units, such as variable-air-volume boxes, to verify that they are accessible and their controls are connected and functioning.

K. Examine plenum ceilings used for supply air to verify that they are airtight. Verify that pipe penetrations and other holes are sealed.

L. Examine strainers for clean screens and proper perforations.

M. Examine three-way valves for proper installation for their intended function of diverting or mixing fluid flows.

N. Examine heat-transfer coils for correct piping connections and for clean and straight fins. 
O. Examine system pumps to ensure absence of entrained air in the suction piping.

P. Examine equipment for installation and for properly operating safety interlocks and controls.

Q. Examine automatic temperature system components to verify the following:

1. 
Dampers, valves, and other controlled devices are operated by the intended controller.

2. 
Dampers and valves are in the position indicated by the controller.
3. 
Integrity of valves and dampers for free and full operation and for tightness of fully 



closed and fully open positions. This includes dampers in multizone units, mixing boxes, 



and variable-air-volume terminals.

TESTING, ADJUSTING, AND BALANCING                                                                    15950-6
MCDEVITT MIDDLE SCHOOL                                           10/16/09

4. Automatic modulating and shutoff valves, including two-way valves and three-way mixing and diverting valves, are properly connected.

5. Thermostats are located to avoid adverse effects of sunlight, drafts, and cold walls.

6. Sensors are located to sense only the intended conditions.

7. Sequence of operation for control modes is according to the Contract Documents.

8. Controller set points are set at indicated values.

9. Interlocked systems are operating.

10. Changeover from heating to cooling mode occurs according to indicated values.

R. 
Report deficiencies discovered before and during performance of TAB procedures. Observe and record system reactions to changes in conditions. Record default set points if different from indicated values.

3.2
PREPARATION

A. Prepare a TAB plan that includes strategies and step-by-step procedures.

B. Complete system readiness checks and prepare system readiness reports. Verify the following:

1. Permanent electrical power wiring is complete.

2. Hydronic systems are filled, clean, and free of air.

3. Automatic temperature-control systems are operational.

4. Equipment and duct access doors are securely closed.

5. Balance, smoke, and fire dampers are open.

6. Isolating and balancing valves are open and control valves are operational.

7. Ceilings are installed in critical areas where air-pattern adjustments are required and access to balancing devices is provided.

8. Windows and doors can be closed so indicated conditions for system operations can be met.

3.3
GENERAL PROCEDURES FOR TESTING AND BALANCING

A. 
Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Testing and Balancing Heating, Ventilating, and Air Conditioning Systems" or "NEBB's "Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems" and this Section.

TESTING, ADJUSTING, AND BALANCING                                                                   15950-7
MCDEVITT MIDDLE SCHOOL                                              10/16/09
B. Cut insulation, ducts, pipes, and equipment cabinets for installation of test probes to the minimum extent necessary to allow adequate performance of procedures. After testing and balancing, close probe holes and patch insulation with new materials identical to those removed. Restore vapor barrier and finish according to insulation Specifications for this Project.

C. 
Mark equipment and balancing device settings with paint or other suitable, permanent identification material, including damper-control positions, valve position indicators, fan-speed​ control levers, and similar controls and devices, to show final settings.

D. 
Take and report testing and balancing measurements in inch-pound (IP) units.

3.4
GENERAL PROCEDURES FOR BALANCING AIR SYSTEMS

A.
Prepare test reports for both fans and outlets. Obtain manufacturer's outlet factors and  recommended testing procedures. Crosscheck the summation of required outlet volumes with required fan volumes.

B. 
For variable-air-volume systems, develop a plan to simulate diversity.

C. 
Determine the best locations in main and branch ducts for accurate duct airflow measurements.

D. 
Check airflow patterns from the outside-air louvers and dampers and the return- and exhaust-air dampers, through the supply-fan discharge and mixing dampers.

E. Locate start-stop and disconnect switches, electrical interlocks, and motor starters.

F. Verify that motor starters are equipped with properly sized thermal protection.

G. Check dampers for proper position to achieve desired airflow path.

H. Check for airflow blockages.

I. Check condensate drains for proper connections and functioning.

J. Check for proper sealing of air-handling unit components.

K. Check for proper sealing of air duct system.

3.5
PROCEDURES FOR CONSTANT-VOLUME AIR SYSTEMS

A.
Adjust fans to deliver total indicated airflows within the maximum allowable fan speed listed by fan manufacturer.

1.
Measure fan static pressures to determine actual static pressure as follows:

a. Measure outlet static pressure as far downstream from the fan as practicable and upstream from restrictions in ducts such as elbows and transitions.

b. Measure static pressure directly at the fan outlet or through the flexible connection.

TESTING, ADJUSTING, AND BALANCING
15950-8

               MCDEVITT MIDDLE SCHOOL                                              10/16/09

          c.      Measure inlet static pressure of single-inlet fans in the inlet duct as near the fan as possible,                             upstream from flexible connection and down stream from duct restrictions.
d.       Measure inlet static pressure of double-inlet fans through the wall of the plenum that   houses the fan.

2. Measure static pressure across each component that makes up an air-handling unit, rooftop unit, and other air-handling and -treating equipment.

a.
Simulate dirty filter operation and record the point at which maintenance personnel must change filters.

3. Measure static pressures entering and leaving other devices such as sound attenuators, under final balanced conditions.

4. Compare design data with installed conditions to determine variations in design static pressures versus actual static pressures. Compare actual system effect factors with calculated system effect factors to identify where variations occur. Recommend corrective action to align design and actual conditions.

5. Obtain approval from Owner for adjustment of fan speed higher or lower than indicated speed. Make required adjustments to pulley sizes, motor sizes, and electrical connections to accommodate fan-speed changes.

6. Do not make fan-speed adjustments that result in motor overload. Consult equipment manufacturers about fan-speed safety factors. Modulate dampers and measure fan-motor amperage to ensure that no overload will occur. Measure amperage in full cooling, full heating, economizer, and any other operating modes to determine the maximum required brake horsepower.

B.
Adjust volume dampers for main duct, submain ducts, and major branch ducts to indicated airflows within specified tolerances.

1. Measure static pressure at a point downstream from the balancing damper and adjust volume dampers until the proper static pressure is achieved.

a. 
Where sufficient space in submain and branch ducts is unavailable for Pitot-tube traverse measurements, measure airflow at terminal outlets and inlets and calculate the total airflow for that zone.

2. Remeasure each submain and branch duct after all have been adjusted. Continue to adjust submain and branch ducts to indicated airflows within specified tolerances.

C.
Measure terminal outlets and inlets without making adjustments.

1.
Measure terminal outlets using latest technology and industry standards equipment.   Electronic ADM & HDM equipment from Shortridge, Alnor or approved equal. Analog equipment will not be accepted. 

TESTING, ADJUSTING, AND BALANCING
15950-9

MCDEVITT MIDDLE SCHOOL                                                         10/16/09

D. 
Adjust terminal outlets and inlets for each space to indicated airflows within specified tolerances of indicated values. Make adjustments using volume dampers rather than extractors and the dampers at air terminals.

1. Adjust each outlet in same room or space to within specified tolerances of indicated quantities without generating noise levels above the limitations prescribed by the Contract Documents.

2. Adjust patterns of adjustable outlets for proper distribution without drafts.

3.6
PROCEDURES FOR VARIABLE-AIR-VOLUME SYSTEMS

A. Compensating for Diversity: When the total airflow of all terminal units is more than the indicated airflow of the fan, place a selected number of terminal units at a maximum set-point airflow condition until the total airflow of the terminal units equals the indicated airflow of the fan. Select the reduced airflow terminal units so they are distributed evenly among the branch ducts.

B. Pressure-Independent, Variable-Air-Volume Systems: After the fan systems have been adjusted, adjust the variable-air-volume systems as follows:

1. Set outside-air dampers at minimum, and return- and exhaust-air dampers at a position that simulates full-cooling load.

2. Select the terminal unit that is most critical to the supply-fan airflow and static pressure. Measure static pressure. Adjust system static pressure so the entering static pressure for the critical terminal unit is not less than the sum of terminal-unit manufacturer's recommended minimum inlet static pressure plus the static pressure needed to overcome terminal-unit discharge system losses.

3. Measure total system airflow. Adjust to within indicated airflow.

4. Set terminal units at maximum airflow and adjust controller or regulator to deliver the designed maximum airflow. Use terminal-unit manufacturer's written instructions to make this adjustment. When total airflow is correct, balance the air outlets downstream from terminal units as described for constant-volume air systems.

5. Set terminal units at minimum airflow and adjust controller or regulator to deliver the designed minimum airflow. Check air outlets for a proportional reduction in airflow as described for constant-volume air systems.

a.
If air outlets are out of balance at minimum airflow, report the condition but leave outlets balanced for maximum airflow.

6. Remeasure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow. Adjust the fan and balance the return-air ducts and inlets as described for constant-volume air systems.

TESTING, ADJUSTING, AND BALANCING
15950-10

MCDEVITT MIDDLE SCHOOL                                                          10/16/09

7. Measure static pressure at the most critical terminal unit and adjust the static-pressure controller at the main supply-air sensing station to ensure that adequate static pressure is maintained at the most critical unit.

8. Record the final fan performance data.

C. 

Pressure-Dependent, Variable-Air-Volume Systems without Diversity: After the fan systems have been adjusted, adjust the variable-air-volume systems as follows:
     1.       Balance systems similar to constant-volume air systems.

2. Set terminal units and supply fan at full-airflow condition.

3. Adjust inlet dampers of each terminal unit to indicated airflow and verify operation of the static-pressure controller. When total airflow is correct, balance the air outlets downstream from terminal units as described for constant-volume air systems.

4. Readjust fan airflow for final maximum readings.

5. Measure operating static pressure at the sensor that controls the supply fan, if one is installed, and verify operation of the static-pressure controller.

6. Set supply fan at minimum airflow if minimum airflow is indicated. Measure static pressure to verify that it is being maintained by the controller.

7. Set terminal units at minimum airflow and adjust controller or regulator to deliver the designed minimum airflow. Check air outlets for a proportional reduction in airflow as described for constant-volume air systems.
a.
If air outlets are out of balance at minimum airflow, report the condition but leave the outlets balanced for maximum airflow.

8. Measure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow. Adjust the fan and balance the return-air ducts and inlets as described for constant-volume air systems.

D. 
Pressure-Dependent, Variable-Air-Volume Systems with Diversity: After the fan systems have been adjusted, adjust the variable-air-volume systems as follows:

1. Set system at maximum indicated airflow by setting the required number of terminal units at minimum airflow. Select the reduced airflow terminal units so they are distributed evenly among the branch ducts. .

2. Adjust supply fan to maximum indicated airflow with the variable-airflow controller set at maximum airflow.

3. Set terminal units at full-airflow condition.

TESTING, ADJUSTING, AND BALANCING
15951-11
MCDEVITT MIDDLE SCHOOL                                                      10/16/09
4. Adjust terminal units starting at the supply-fan end of the system and continuing progressively to the end of the system. Adjust inlet dampers of each terminal unit to indicated airflow. When total airflow is correct, balance the air outlets downstream from terminal units as described for constant-volume air systems.

5. Adjust terminal units for minimum airflow.

6. Measure static pressure at the sensor.

7. Measure the return airflow to the fan while operating at maximum return airflow and minimum outside airflow. Adjust the fan and balance the return-air ducts and inlets as described for constant-volume air systems.

3.7
GENERAL PROCEDURES FOR HYDRONIC SYSTEMS

A. Prepare test reports with pertinent design data and number in sequence starting at pump to end of system. Check the sum of branch-circuit flows against approved pump flow rate. Correct variations that exceed plus or minus 5 percent.

B. Prepare schematic diagrams of systems' "as built" piping layouts.

C. Prepare hydronic systems for testing and balancing according to the following, in addition to the general preparation procedures specified above:

1. Open all manual valves for maximum flow.

2. Check expansion tank liquid level.

3. Check makeup-water-station pressure gage for adequate pressure for highest vent.

4. Check flow-control valves for specified sequence of operation and set at indicated flow.

5. Set differential pressure control valves at the specified differential pressure. Do not set at fully closed position when pump is positive-displacement type unless several terminal valves are kept open.

6. Set system controls so automatic valves are wide open to heat exchangers.

7.
Check pump-motor load. If motor is overloaded, throttle main flow-balancing device so  
motor nameplate rating is not exceeded.

8.         Check air vents for a forceful liquid flow exiting from vents when manually operated.

3.8.
PROCEDURES FOR HYDRONIC SYSTEMS

A. 
Measure water flow at pumps. Use the following procedures, except for positive-displacement pumps:

1.
Verify impeller size by operating the pump with the _discharge valve closed. Read pressure differential across the pump. Convert pressure to head and correct for

TESTING, ADJUSTING, AND BALANCING
15950-12
MCDEVITT MIDDLE SCHOOL
10/16/09
differences in gage heights. Note the point on manufacturer's pump curve at zero flow and verify that the pump has the intended impeller size.

2. 
Check system resistance. With all valves open, read pressure differential across the pump and mark pump manufacturer's head-capacity curve. Adjust pump discharge valve until indicated water flow is achieved.
3.
Verify pump-motor brake horsepower. Calculate, the intended brake horsepower for the system based on pump manufacturer's performance data. Compare calculated brake horsepower with nameplate data on the pump motor. Report conditions where actual amperage exceeds motor nameplate amperage.

4.
Report flow rates that are not within plus or minus 5 percent of design.

B.
Set calibrated balancing valves, if installed, at calculated presettings.

C.
Measure flow at all stations and adjust, where necessary, to obtain first balance.

1.
System components that have Cv rating or an accurately cataloged flow-pressure-drop relationship may be used as a flow-indicating device.

D. 
Measure flow at main balancing station and set main balancing device to achieve flow that is 5 percent greater than indicated flow.

E.
Adjust balancing stations to within specified tolerances of indicated flow rate as follows:

1. Determine the balancing station with the highest percentage over indicated flow.

2. Adjust each station in turn, beginning with the station with the highest percentage over  indicated flow and proceeding to the station with the lowest percentage over indicated flow.
3. Record settings and mark balancing devices.

F. 
Measure pump flow rate and make final measurements of pump amperage, voltage, rpm, pump heads, and systems' pressures and temperatures including outdoor-air temperature.
G.
Measure the differential-pressure control valve settings existing at the conclusions of balancing.

3.9
PROCEDURES FOR VARIABLE-FLOW HYDRONIC SYSTEMS

A. 
Balance systems with automatic two- and three-way control valves by setting systems at maximum flow through heat-exchange terminals and proceed as specified above for hydronic systems.

3.10 PROCEDURES FOR MOTORS

A.
Motors, 1/2 HP and Larger: Test at final balanced conditions and record the following data:

1.
Manufacturer, model, and serial numbers.

TESTING, ADJUSTING, AND BALANCING
15950-13

MCDEVITT MIDDLE SCHOOL

. 10/16/09
2. Motor horsepower rating.

3. Motor rpm.

4. Efficiency rating.

5. Nameplate and measured voltage, each phase.

6. Nameplate and measured amperage, each phase.

7. Starter thermal-protection-element rating.

B. 
Motors Driven by Variable-Frequency Controllers: Test for proper operation at speeds varying from minimum to maximum. Test the manual bypass for the controller to prove proper operation: Record observations, including controller manufacturer, model and serial numbers, and nameplate data.

3.11 PROCEDURES FOR CHILLER

A. 
Balance water flow through evaporator to within specified tolerances of indicated flow with all pumps operating. Do not exceed the flow for the maximum tube velocity recommended by the chiller manufacturer. Measure and record the following data at design conditions:

1. Evaporator-water entering and leaving temperatures, pressure drop, and water flow.

2. Evaporator and condenser refrigerant temperatures and pressures, using instruments furnished by chiller manufacturer.

3. Power factor if factory-installed instrumentation is furnished for measuring kilowatt.

4. Kilowatt input if factory-installed instrumentation is furnished for measuring kilowatt.

5. Capacity: Calculate in tons of cooling.

6.       Air-cooled chillers, verify condenser-fan rotation and record fan and motor data including number of fans and entering- and leaving-air temperatures.

3.12 PROCEDURES FOR CONDENSING UNITS

A. Verify proper rotation of fans.

B. Measure entering- and leaving-air temperatures.

C. Record compressor data. 
3.13 PROCEDURES FOR BOILERS

A.
If hydronic, measure entering- and leaving-water temperatures and water flow.

TESTING, ADJUSTING AND BALANCING
15950-14

MCDEVITT MIDDLE SCHOOL
10/16/09
3.14 
   PROCEDURES FOR HEAT-TRANSFER COILS

A.
Water Coils: Measure the following data for each coil:

1. Entering- and leaving-water temperature.

2. Water flow rate.

3. Water pressure drop.

4. Dry-bulb temperature of entering and leaving air.
5. Wet-bulb temperature of entering and leaving air for cooling coils.

6. Airflow.

7. Air pressure drop.

B.
Electric-Heating Coils: Measure the following data for each coil:

1. Nameplate data.

2. Airflow.

3. Entering- and leaving-air temperature at full load.

4. Voltage and amperage input of each phase at full load and at each incremental stage.

5. Calculated kilowatt at full load.

6. Fuse or circuit-breaker rating for overload protection.

C.
Refrigerant Coils: Measure the following data for each coil:

1. Dry-bulb temperature of entering and leaving air.

2. Wet-bulb temperature of entering and leaving air.

3. Airflow.

4. Air pressure drop.

5. Refrigerant suction pressure and temperature. 
3.15 
PROCEDURES FOR TEMPERATURE MEASUREMENTS

A.
During TAB, report the need for adjustment in temperature regulation within the automatic 
temperature-control system.

TESTING, ADJUSTING, AND BALANCING
15950-15

MCDEVITT MIDDLE SCHOOL
10/16/09
B. Measure indoor wet- and dry-bulb temperatures every other hour for a period of two successive eight-hour days, in each separately controlled zone, to prove correctness of final temperature settings. Measure when the building or zone is occupied.

C. Measure outside-air, wet- and dry-bulb temperatures.

3.16 
 TEMPERATURE-CONTROL VERIFICATION

A. Verify that controllers are calibrated and commissioned.

B. Check transmitter and controller locations and note conditions that would adversely affect control functions.

C. Record controller settings and note variances between set points and actual measurements.

D. Check the operation of limiting controllers (i.e., high- and low-temperature controllers).

E. Check free travel and proper operation of control devices such as damper and valve operators.

F. Check the sequence of operation of control devices. Note air pressures and device positions and correlate with airflow and water flow measurements. Note the speed of response to input changes.

G. Check the interaction of electrically operated switch transducers.

H. Check the interaction of interlock and lockout systems.

I. Record voltages of power supply and controller output. Determine whether the system operates on a grounded or nongrounded power supply.

J. Note operation of electric actuators using spring return for proper fail-safe operations.

3.17
TOLERANCES

A. 
  Set HVAC system airflow and water flow rates within the following tolerances:

1. Supply, Return, and Exhaust Fans and Equipment with Fans: Plus 5 to plus 10 percent.

2. Air Outlets and Inlets: 0 to minus 10 percent.

3. Heating-Water Flow Rate: 0 to minus 10 percent.

4. Cooling-Water Flow Rate: 0 to minus 5 percent.

3.18
REPORT

A.
General: Typewritten, or computer printout in letter-quality font, on standard bond paper, in three-ring binder, tabulated and divided into sections by tested and balanced systems.

TESTING, ADJUSTING, AND BALANCING
15950-16

MCDEVITT MIDDLE SCHOOL                                                      10/16/09

B.
Include a certification sheet in front of binder signed and sealed by the certified testing and balancing engineer.

1.
Include a list of instruments used for procedures, along with proof of calibration.

C.
Final Report Contents: In addition to certified field report data, include the following:

1. Pump curves.

2. Fan curves.

3. Manufacturers' test data.

4. Field test reports prepared by system and equipment installers.

5. Other information relative to equipment performance, but do not include Shop Drawings  and Product Data.

D.
General Report Data: In addition to form titles and entries, include the following data in the final report, as applicable:

1. Title page.

2. Name and address of TAB firm.
3. Project name.

4. Project location.

5. Architect's name and address.

6. Engineer's name and address.

7. Contractor's name and address.

              8.
         Report date.

9. Signature of TAB firm who certifies the report.

10. Table of Contents with the total number of pages defined for each section of the report 
Number each page in the report.

11. Summary of contents including the following:

a. Indicated versus final performance.

b. Notable characteristics of systems.

TESTING, ADJUSTING, AND BALANCING
15950-17

MCDEVITT MIDDLE SCHOOL
10/16/09
c.
Description of system operation sequence if it varies from the Contract Documents.

12. Nomenclature sheets for each item of equipment.

13. Data for terminal units, including manufacturer, type size, and fittings.

14. Notes to explain why certain, final data in the body of reports varies from indicated values.

15.   Test conditions for fans and pump performance forms including the following:

a. Settings for outside-, return-, and exhaust-air dampers.

b. Conditions of filters.

c. Cooling coil, wet- and dry-bulb conditions.

d. Face and bypass damper settings at coils.

e. Fan drive settings including settings and percentage of maximum pitch diameter.

f. Inlet vane settings for variable-air-volume systems.

g. Settings for supply-air, static pressure controller.

h. Other system operating conditions that affect performance.

E.
Air-Handling Unit Test Reports: For air-handling units with coils, include the following:

1.
Unit Data: Include the following:

a. Unit identification.

b. Location.

c. Make and type.

d. Model number and unit size.

e. Manufacturer's serial number.

f. Unit arrangement and class.

g. Discharge arrangement.

h. Sheave make, size in inches, and bore.

i. Sheave dimensions, center-to-center, and amount of adjustments in inches.

TESTING, ADJUSTING, AND BALANCING
15950-18

MCDEVITT MIDDLE SCHOOL                                                          10/16/09

j. Number of belts, make, and size.

k. Number of filters, type, and size.

2.
Motor Data

	a.
	Make and frame type and size.

	b.
	Horsepower and rpm.

	c.
	Volts, phase, and hertz.

	d.
	Full-load amperage and service factor.

	e.
	Sheave make, size in inches, and bore.

	f.
	Sheave dimensions, center-to-center, and amount of adjustments in inches.

	3.
Test Data (Indicated and Actual Values)

	a.
	Total airflow rate in cfm.

	b.
	Total system static pressure in inches wg.

	c.
	Fan rpm.

	d.
	Discharge static pressure in inches wg.

	e.
	Filter static-pressure differential in inches wg.

	f.
	Preheat coil static-pressure differential in inches wg.

	g.
	Cooling coil static-pressure differential in inches wg.

	h.
	Heating coil static-pressure differential in inches wg.

	i.
	Outside airflow in cfm.

	j.
	Return airflow in cfm.

	k.
	Outside-air damper position.

	1.
	Return-air damper position.

	m.
	Vortex damper position.

	F.
Apparatus-Coil Test Reports:


1. Coil Data

TESTING, ADJUSTING, AND BALANCING
15950-19

MCDEVITT MIDDLE SCHOOL                                                   10/16/09
	a.
	System identification.

	b.
	Location.

	c.
	Coil type.

	d.
	Number of rows.

	e.
	Fin spacing in fins per inch o.c.

	f.
	Make and model number.

	g.
	Face area in sq. ft.

	h.
	Tube size in NPS.

	i.
	Tube and fm materials.

	j.
	Circuiting arrangement.

	2.
Test Data (Indicated and Actual Values)

	a. 
	Airflow rate in cfm.

	b.
	Average face velocity in fpm.

	c.
	Air pressure drop in inches wg.

	d.
	Outside-air, wet- and dry-bulb temperatures in deg F.

	e.
	Return-air, wet- and dry-bulb temperatures in deg F.

	f.
	Entering-air, wet- and dry-bulb temperatures in deg F.

	g.
	Leaving-air, wet- and dry-bulb temperatures in deg F.

	h.
	Water flow rate in gpm.

	i.
	Water pressure differential in feet of head or psig.

	j.
	Entering-water temperature in deg F.

	k.
	Leaving-water temperature in deg F.

	1.
	Refrigerant expansion valve and refrigerant types.

	m.
	Refrigerant suction pressure in psig.

	n.
	Refrigerant suction temperature in deg F.


TESTING, ADJUSTING, AND BALANCING
15950-20

MCDEVITT MIDDLE SCHOOL
10/16/09
o.
Inlet steam pressure in psig.

G.
Gas-Fired Heat Apparatus Test Reports: In addition to manufacturer's factory startup equipment reports, include the following:

1.
Unit Data

a. System identification.

b. Location.

c. Make and type.

d. Model number and unit size.

e. Manufacturer's serial number.

f. Fuel type in input data.

g. . Output capacity in Btuh.

h. Ignition type.

i. Burner-control types.

j. Motor horsepower and rpm.

k. Motor volts, phase, and hertz.

1.        Motor full-load amperage and service factor.

m. Sheave make, size in inches, and bore.

n. Sheave dimensions, center-to-center, and amount of adjustments in inches.

2.
Test Data (Indicated and Actual Values)

a. Total airflow rate in cfm.

b. Entering-air temperature in deg F.

c. Leaving-air temperature in deg F.

d. Air temperature differential in deg F.

e. Entering-air static pressure in inches wg.

f. Leaving-air static pressure in inches wg.

TESTING, ADJUSTING, AND BALANCING
15950-21

g. Air static-pressure differential in inches wg.

h. Low-fire fuel input in Btuh.

i. High-fire fuel input in Btuh.

j. Manifold pressure in psig.

k. High-temperature-limit setting in deg F.

l.
Operating set point in Btuh.

m. Motor voltage at each connection.

n. Motor amperage for each phase.

o. Heating value of fuel in Btuh.

H.
Fan Test Reports: For supply, return, and exhaust fans; include the following:

1.
Fan Data

a. System identification.

b. Location.

c. Make and type.

d. Model number and size.

e. Manufacturer's serial number.

f. Arrangement and class.

g. Sheave make, size in inches, and bore.

h. Sheave dimensions, center-to-center, and amount of adjustments in inches.

2.
Motor Data

a. Make and frame type and size.

b. Horsepower and rpm.

c. Volts, phase, and hertz.

d. Full-load amperage and service factor.

e. Sheave make, size in inches, and bore.

TESTING, ADJUSTING, AND BALANCING
    15950-2

MCDEVITT MIDDLE SCHOOL
10/16/09
f. Sheave dimensions, center-to-center, and amount of adjustments in inches.

g. Number of belts, make, and size.

3.
Test Data (Indicated and Actual Values)

a. Total airflow rate in cfm.

b. Total system static pressure in inches wg.

c. Fan rpm.

d. Discharge static pressure in inches wg.

e. Suction static pressure in inches wg.

I.
Round, Flat-Oval, and Rectangular Duct Traverse Reports: Include a diagram with a grid representing the duct cross-section and record the following:

1.
Report Data

a.
System and air-handling unit number.

	b.
	Location and zone.

	c.
	Traverse air temperature in deg F.'

	d.
	Duct static pressure in inches wg

	e.
	Duct size in inches.

	f.
	Duct area in sq. ft...

	g.
	Indicated airflow rate in cfm.

	h.
	Indicated velocity in fpm.

	i.
	Actual airflow rate in cfm.

	j.
	Actual average velocity in fpm.

	k.
	Barometric pressure in prig.

	J.
Air-Terminal-Device Reports:


1.
Unit Data

a.
System and air-handling unit identification.

TESTING, ADJUSTING, AND BALANCING
15950-23

MCDEVITT MIDDLE SCHOOL                                            10/16/09

b. Location and zone.

c. Test apparatus used.

	d.
	Area served.

	e.
	Air-terminal-device make.

	f.
	Air-terminal-device number from system diagram.

	g.
	Air-terminal-device type and model number.

	h.
	Air-terminal-device size.

	i.
	Air-terminal-device effective area in sq. ft..

	2.

	Test Data (Indicated and Actual Values)

	a.
	Airflow rate in cfm.

	b.
	Air velocity in fpm.

	c.
	Preliminary airflow rate as needed in cfm.

	d.
	Preliminary velocity as needed in fpm.

	e.
	Final airflow rate in cfm.

	£
	Final velocity in fpm.

	g.
	Space temperature in deg F.

	K.
System-Coil Reports: For reheat coils and water coils of terminal units, include the following:


1.
Unit Data

a.
System and air-handling unit identification.

	b.
	Location and zone.

	c.
	Room or riser served.

	d.
	Coil make and size.

	e.
	Flow meter type.

	2.
Test Data (Indicated and Actual Values)

	a.
	Airflow rate in cfm.


TESTING, ADJUSTING, AND BALANCING                                                              15950-20

MCDEVITT MIDDLE SCHOOL 
10/16/09
	b.
	Entering-water temperature in deg F.

	c.
	Leaving-water temperature in deg F.

	d.
	Water pressure drop in feet of head or psig.

	e.
	Entering-air temperature in deg F.

	f.
	Leaving-air temperature in deg F.

	L.
Packaged Chiller Reports:

	1.
Unit Data

	a.
	Unit identification.

	b.
	Make and model number.

	c.
	Manufacturer's serial number.

	d.
	Refrigerant type and capacity in gal.

	e.
	Starter type and size.

	f.
	Starter thermal protection size.

	g.
	Compressor make and model number.

	h.
	Compressor manufacturer's serial number.

	2.
Air-Cooled Condenser Test Data (Indicated and Actual Values)

	a.
	Refrigerant pressure in psig.

	b.
	Refrigerant temperature in deg F.

	c.
	Entering- and leaving-air temperature in deg F.

	3.
Evaporator Test Reports (Indicated and Actual Values)

	a.
	Refrigerant pressure in psig.

	b.
	Refrigerant temperature in deg F.

	c.
	Entering-water temperature in deg F.

	d.
	Leaving-water temperature in deg F.

	e.
	Entering-water pressure in feet of head or psig.


TESTING, ADJUSTING, AND BALANCING
15950 -25

f.
Water pressure differential in feet of head or psig.

4.
Compressor Test Data (Indicated and Actual Values)

a. Suction pressure in psig.

b. Suction temperature in deg F.

c. Discharge pressure in psig.

d. Discharge temperature in deg F.

e. Oil pressure in psig.

f. Oil temperature in deg F.

g. Voltage at each connection.

h. Amperage for each phase.

i. Kilowatt input.

j. Crankcase heater kilowatt.

k. Chilled-water control set point in deg F.

1.
Condenser-water control set point in deg F.

m. Refrigerant low-pressure-cutoff set point in psig.

n. Refrigerant high-pressure-cutoff set point in psig.

5.
Refrigerant Test Data (Indicated and Actual Values)

a.
Oil level.

b.
Refrigerant level.

c. Relief valve setting in psig.

d. Unloader set points in psig.

e. Percentage of cylinders unloaded.

f. Bearing temperatures in deg F.

g. Vane position.

h. Low-temperature-cutoff set point in deg F.

TESTING, ADJUSTING, AND BALANCING
15950-26

MCDEVITT MIDDLE SCHOOL
10/16/09
M. 
Compressor and Condenser Reports: For refrigerant side of unitary systems, stand-alone refrigerant compressors, air-cooled condensing units, or water-cooled condensing units, include the following:

	1.
Unit Data

	a.
	Unit identification.

	b.
	Location.

	c.
	Unit make and model number.

	d.
	Compressor make.

	e.
	Compressor model and serial numbers.

	f.
	Refrigerant weight in lb (kg).

	g.
	Low ambient temperature cutoff in deg F (deg C).

	2.
Test
	Data (Indicated and Actual Values)

	a.
	Inlet-duct static pressure in inches wg.

	b.
	Outlet-duct static pressure in inches wg.

	c.
	Entering-air, dry-bulb temperature in deg F.

	d.
	Leaving-air, dry-bulb temperature in deg F.

	e.
	Condenser entering-water temperature in deg F.

	f.
	Condenser leaving-water temperature in deg F.

	g.
	Condenser-water temperature differential in deg F.

	h.
	Condenser entering-water pressure in feet of head or psig.

	i.
	Condenser leaving-water pressure in feet of head or psig.

	j.
	Condenser-water pressure differential in feet of head or psig.

	k.
	Control settings.

	1.
	Unloader set points.

	m.
	Low-pressure-cutout set point in psig.

	n.
	High-pressure-cutout set point in psig.


TESTING, ADJUSTING, AND BALANCING
15950-27

MCDEVITT MIDDLE SCHOOL
10/16/09
o. Suction pressure in psig

p. Suction temperature in deg F.

q. Condenser refrigerant pressure in psig.

r. Condenser refrigerant temperature in deg F.

s. Oil pressure in psig.

t. Oil temperature in deg F.

u. Voltage at each connection.

v. Amperage for each phase:

w. Kilowatt input.

x. Crankcase heater kilowatt.

y. Number of fans.

z. Condenser fan rpm.

aa. Condenser fan airflow rate in cfm.

ab. Condenser fan motor make, frame size, rpm, and horsepower 

ac. Condenser fan motor voltage at each connection.

dd. Condenser fan motor amperage for each phase.

N. 
Pump Test Reports: Calculate impeller size by plotting the shutoff head on pump curves and include the following:

1.
Unit Data

a. Unit identification.

b. Location.

c. Service.

d. Make and size.

e. Model and serial numbers.

f. Water flow rate in gpm.

g. Water pressure differential in feet of head or psig
TESTING, ADJUSTING, AND BALANCING
15950-28

MCDEVITT MIDDLE SCHOOL
10/16/09
	h.
	Required net positive suction head in feet of head or psig.

	i.
	Pump rpm.

	j.
	Impeller diameter in inches.

	k.
	Motor make and frame size.

	1.
	Motor horsepower and rpm.

	m.
	Voltage at each connection.

	n.
	Amperage for each phase.

	o.
	Full-load amperage and service factor.

	p.
	Seal type.

	2.
Test
	Data (Indicated and Actual Values)

	a.
	Static head in feet of head or psig.

	b.
	Pump shutoff pressure in feet of head or psig.

	c.
	Actual impeller size in inches.

	d.
	Full-open flow rate in gpm.

	e.
	Full-open pressure in feet of head or psig.

	f.
	Final discharge pressure in feet of head or psig.

	g.
	Final suction pressure in feet of head or psig.

	h.
	Final total pressure in feet of head or psig.

	i.
	Final water flow rate in gpm.

	j.
	Voltage at each connection.

	k
	Amperage for each phase.

	O.
Instrument
	Calibration Reports:


1.
Report Data

a. Instrument type and make.

b. Serial number.

TESTING, ADJUSTING, AND BALANCING
15950-29

MCDEVITT MIDDLE SCHOOL
10/16/09
c. Application.

d. Dates of use.

e. Dates of calibration.

3.19
INSPECTIONS

A.
Initial Inspection:

                       After testing and balancing are complete, operate each system and randomly check measurements to verify that the system is operating according to the final test and balance readings documented in the Final Report.
1. Randomly check the following for each system:

a. Measure airflow of at least 10 percent of air outlets:

b. Measure water flow of at least 5 percent of terminals.

c. Measure room temperature at each thermostat/temperature sensor. Compare the   reading to the set point.

d. Verify that balancing devices are marked with final balance position.

e. Note deviations to the Contract Documents in the Final Report.

B.
Final Inspection:

1. After initial inspection is complete and evidence by random checks verifies that testing and balancing are complete and accurately documented in the final report, request that a final inspection be made by Owners Representative
2. TAB firm test and balance engineer shall conduct the inspection in the presence of Owners Representative.

3. Independent Balancing Firm shall randomly select measurements documented in the final report to be rechecked. The rechecking shall be limited to either 10 percent of the total measurements recorded, or the extent of measurements that can be accomplished in a normal 8-hour business day.

4. If the rechecks yield measurements that differ from the measurements documented in the final report by more than the tolerances allowed, the measurements shall be noted as "FAILED."

5. If the number of "FAILED" measurements is greater than 10 percent of the total measurements checked during the final inspection, the testing and balancing shall be considered incomplete and shall be rejected.

TESTING, ADJUSTING, AND BALANCING

15950-30


10/16/09
6. TAB firm shall recheck all measurements and make adjustments. Revise the final report and balancing device settings to include all changes and resubmit the final report.

7. Request a second final inspection. If the second final inspection also fails, Owner shall contract the services of another TAB firm to complete the testing and balancing in accordance with the Contract Documents and deduct the cost of the services from the final payment.

3.20 ADDITIONAL TESTS

A.
Within 90 days of completing TAB, perform additional testing and balancing to verify that 
balanced conditions are being maintained throughout and to correct unusual conditions.

B.
Seasonal Periods: If initial TAB procedures were not performed during near-peak summer and 
winter conditions, perform additional testing, inspecting, and adjusting during near-peak summer 
and winter conditions.

END OF SECTION  15950 
